## types
type | name | pk
int | regulation_id
string | regulation_name
float | max_storage_kg
float | safety_distance_m
float | max_pressure_bar
string | documentation_link

## regulations
regulation_id | regulation_name | regulation_info | storage_gal_min | storage_gal_max | safety_distance_ft | max_pressure_bar | documentation_link
0 | OSHA 1910.103(c)(2)(ii)(b)' | distance between lh2 and flammale liquids or buildings' | 0 | 3500 | 50
1 | OSHA 1910.103(c)(2)(ii)(b)' | distance between lh2 and flammale liquids or buildings' | 0 | 15000 | 75
2 | OSHA 1910.103(c)(2)(ii)(b)' | distance between lh2 and flammable liquids or buildings' | 0 | 30000 | 100
3 | OSHA 1910.103(c)(2)(ii)(b)' | distance between lh2 and solid lh2' | 0 | 30000 | 5
4 | OSHA 1910.103(c)(2)(ii)(b)' | distance between lh2 and people' | 3500 |  | 75
5 | DOT 49.B.III.B.397 | distance between lh2 and open fire' | 0 |  | 300
6 | OSHA 1910.119(d)' | handling of hazardous materials will follow safety protocols | 16830
7 | J2600_201510 4.2.2 | nozzle and receptacle designs shall prevent vehicles from being fueled with a pressure class greater than vehicle
8 | J2600_201510 4.2.3 | nozzle and receptacle designs shall be designed to operate properly with a local ambient temperature of –40 to 65 °C
9 | J2600_201510 4.2.4.5 | materials used in construction of nozzles, receptacles, and dust caps shall be non-sparking or spark-reducing
10 | J2600_201510 4.2.4.6 | Nozzles and receptacles shall be designed so that they are either tolerant of solid contamination, or have a means to protect themselves from said contamination when connected or disconnected
11 | J2600_201510 4.3.7.8 | The receptacle/fuel storage connection shall be able to withstand normal abuse encountered in the installation and maintenance process without damage or deformation to the joint
12 | J2600_201510 5.5.3 | At the end of the test procedure, the samples shall not exhibit evidence of explosive decompression damage, swelled more than 25%, have shrunk more than 1%, or have incurred a weight loss of more than 10%.